NTU SPACE DATA CENTER

SDTwin POWER MODULE

Power Module Software Test Report

Solar Array  Battery Response  Power Allocation  Protection  Simulink Comparison

| Institute | College of Computing and Data Science, Nanyang Technological University |
| --- | --- |
| Author | Automated verification and report generation |
| Reviewer |  |
| Issue date | 7 October 2026 |

College of Computing and Data Science, Nanyang Technological University

Version Control

| Abstract | This report records the framework, inputs, criteria and individual comparisons of the Power model with independent Simulink simulation. All 20 numerical comparisons pass; 17 cases pass design acceptance and 3 fail due to the full-charge constraint. |  |  |  |
| --- | --- | --- | --- | --- |
| Keywords | Power model; Simulink; test cases; numerical comparison; acceptance records |  |  |  |
| Change Record |  |  |  |  |
| Revision | Change Request | Date | Author | Description |
| 1.0 | Test execution | 2026-10-07 |  | Executed 20 model comparisons with Simulink and retained all results. |
| 1.1 | Standard format | 2026-10-07 |  | Applied the Orbit seven-chapter layout, case records and landscape summary; data and criteria unchanged. |

TABLE OF CONTENTS

1 Overview	1

1.1 Identification	1

1.2 Software and Document Overview	1

1.3 Abbreviations and Conventions	1

2 Test Content	2

2.1 Functional Requirement and Test Case Traceability	2

2.2 Comparison Framework	3

3 Detailed Test Projects	4

3.1 Solar Array and Battery Components	4

3.1.1 Test Project 1 Solar irradiance and panel attitude	4

3.1.2 Test Project 2 Open circuit voltage and initial charge	7

3.1.3 Test Project 3 Charge and discharge voltage versus temperature	9

3.1.4 Test Project 4 Battery heat and reversible heat sign	12

3.1.5 Test Project 5 Cell to series and parallel pack scaling	14

3.2 Power Allocation and Protection Interfaces	16

3.2.1 Test Project 6 Solar and battery power allocation	16

3.2.2 Test Project 7 Distribution efficiency and loss	19

3.2.3 Test Project 8 Charge limits and solar curtailment	21

3.2.4 Test Project 9 Discharge capability and supply shortfall	23

3.2.5 Test Project 10 Charging boundary at full state of charge	25

3.2.6 Test Project 11 Protection commands and latched states	27

3.2.7 Test Project 12 Invalid inputs and state boundaries	29

3.3 Dynamic Supply and Electrothermal Processes	31

3.3.1 Test Project 13 Charging under continuous sunlight	31

3.3.2 Test Project 14 Eclipse entry and exit	33

3.3.3 Test Project 15 Compute load steps	35

3.3.4 Test Project 16 Dynamic charge curtailment	37

3.3.5 Test Project 17 Supply loss latch and explicit restart	39

3.3.6 Test Project 18 Battery electrothermal feedback	41

3.3.7 Test Project 19 Energy balance over three orbit cycles	43

3.4 Numerical Accuracy Review	45

3.4.1 Test Project 20 Solver convergence and accuracy review	45

4 Test Content Sufficiency Analysis	47

5 Test Conditions and Requirements	48

5.1 Execution Environment and Acceptance Criteria	48

5.2 Baseline Scenario and Input Requirements	48

6 Test Data	50

6.1 Battery Material Parameters	50

6.2 Data Inventory and Reproduction	51

6.3 Integrated Energy Comparison Data	52

6.4 Numerical Convergence Data	53

7 Test Summary	54

7.1 Anomalies and Conclusion	56

1 Overview

1.1 Identification

Platform: SDTwin. Module: Power. Document revision: 1.1. Test date: 7 October 2026.

Purpose: record repeatable comparison tests of the project model against Simulink and the actual acceptance verdicts.

1.2 Software and Document Overview

This report compares the project Power model with Simulink under identical parameters, states and inputs. Tests cover array power, cell voltage and heat, pack scaling, allocation, protection commands, dynamic trajectories, conservation and numerical precision.

Table 1. System Under Test and Reference Implementation

| Object | Implementation and boundary |
| --- | --- |
| Project model | Thermal/sdtwin_sim/power_stand_in.py |
| Implementation status | A test implementation of the Power design report, not production EPS software. The source under test is unchanged. |
| Simulink | Independent MATLAB equations in a Level 2 S-function in a real .slx model, with continuous states integrated by Simulink ode45. |
| Independence | Only input parameters are shared. MATLAB does not call Python; Python does not take Simulink outputs as its state trajectory. |
| Parameter provenance | Existing illustrative array and battery assets, including illustrative electrode polynomials, not fitted to a selected physical cell. |
| Supported conclusion | Cross-implementation verification under common physics assumptions and selected design behavior checks. This is neither measured validation nor a comparison against a factory Simscape battery block. |

Observed conclusion

All 20 projects executed and passed numerical comparison. CT-003, DY-002 and DY-007 fail full-charge behavior requirements. Both implementations constrain current, voltage and material fractions but omit the configured 100% usable-charge endpoint from the charging constraint.

Failed cases retain their inputs and raw results. The model under test was not changed, tolerances were not relaxed, and SOC was not clipped to hide the failures.

1.3 Abbreviations and Conventions

Table 2. Abbreviations and Symbols

| Term | Definition |
| --- | --- |
| SOC | Usable charge fraction: zero is empty and one is full. |
| PDU | Power distribution unit; losses follow the specified efficiency. |
| RMSE | Root mean square error at identical samples. |
| G / cos θ | Irradiance including eclipse and panel incidence cosine. |
| i / PB | Positive for discharge, negative for charge. |

2 Test Content

Twenty projects form four capability groups. Each maps to one detailed case record and one final summary record. Numerical agreement and design behavior are evaluated and recorded separately.

2.1 Functional Requirement and Test Case Traceability

Table 3. Functional Requirement and Test Case Traceability

| No. | Case ID | Function | Test Name | Basis | Status |
| --- | --- | --- | --- | --- | --- |
| 1 | PV-001 | solar_power | Solar irradiance and panel attitude | P2 | Pass |
| 2 | BT-001 | battery_response | Open circuit voltage and initial charge | P4–P8, P10 | Pass |
| 3 | BT-002 | battery_response | Charge and discharge voltage versus temperature | P4–P8, P10 | Pass |
| 4 | BT-003 | battery_response | Battery heat and reversible heat sign | P4–P8, P10 | Pass |
| 5 | BT-004 | battery_response | Cell to series and parallel pack scaling | P4–P8, P10 | Pass |
| 6 | PD-001 | solve_power_allocation | Solar and battery power allocation | P1, P3, P11 | Pass |
| 7 | PD-002 | solve_power_allocation | Distribution efficiency and loss | P1, P3, P11 | Pass |
| 8 | CT-001 | solve_power_allocation | Charge limits and solar curtailment | P1, P3, P11 | Pass |
| 9 | CT-002 | solve_power_allocation | Discharge capability and supply shortfall | P1, P3, P11 | Pass |
| 10 | CT-003 | solve_power_allocation | Charging boundary at full state of charge | P1, P3, P11 | Fail |
| 11 | PR-001 | apply_power_event | Protection commands and latched states | 5 | Pass |
| 12 | IV-001 | PowerInputs / PowerState | Invalid inputs and state boundaries | 5 | Pass |
| 13 | DY-001 | solve_power_allocation / state integration | Charging under continuous sunlight | P1–P11 | Pass |
| 14 | DY-002 | solve_power_allocation / state integration | Eclipse entry and exit | P1–P11 | Fail |
| 15 | DY-003 | solve_power_allocation / state integration | Compute load steps | P1–P11 | Pass |
| 16 | DY-004 | solve_power_allocation / state integration | Dynamic charge curtailment | P1–P11 | Pass |
| 17 | DY-005 | solve_power_allocation / state integration | Supply loss latch and explicit restart | P1–P11 | Pass |
| 18 | DY-006 | solve_power_allocation / state integration | Battery electrothermal feedback | P1–P11 | Pass |
| 19 | DY-007 | solve_power_allocation / state integration | Energy balance over three orbit cycles | P1–P11 | Fail |
| 20 | NU-001 | DOP853 / ode45 | Solver convergence and accuracy review | P1–P11 | Pass |

2.2 Comparison Framework

Table 4. Test Framework and Execution Contract

| Stage | Execution contract |
| --- | --- |
| Shared inputs | suite.json stores device parameters, initial conditions, input combinations, event times, numerical settings and thresholds, bound by SHA256. |
| Independent execution | Python calls the existing API with SciPy DOP853 integration; MATLAB independently evaluates cell and allocation equations while Simulink ode45 integrates states. |
| Events and time | Scheduled discontinuities split integration intervals exactly. Both left and right values are retained at each boundary. Protection is applied only at accepted boundaries. |
| Signal comparison | Subtract values at the same time, side and unit. No interpolation crosses an event. Invalid results compare validity and event flags without replacing missing ports by zero. |
| Independent acceptance | In addition to numerical agreement, check power and lithium conservation, solar feasibility, usable SOC range, full-charge stopping and expected protection behavior. |
| Evidence and report | Retain both CSV trajectories, direct difference CSVs, event JSON, check verdicts and source hashes. Every case includes an input table, error table and comparison figure. |

Physical relations and states

Ppv + PB = Pload + QD     PB = Ns Np i v     Pload = ηD Pbus

dxn/dt = −i/Qn     dxp/dt = i/Qp     SOC = (xn − xn,0)/(xn,100 − xn,0)

Positive cell current and battery power denote discharge; negative values denote charging. QB is internal battery heat and is not subtracted again from terminal-power balance. Battery temperature is integrated once in the thermal domain.

Electrothermal cases use CB dTB/dt = QB − (TB − Tsink)/R. Other dynamic cases prescribe a constant temperature and do not run a second temperature model.

3 Detailed Test Projects

Every project uses the Orbit test report record fields. Input tables specify the scenario; result pages retain both outputs, direct differences and error tables. Human signature fields are intentionally blank.

3.1 Solar Array and Battery Components

3.1.1 Test Project 1 Solar irradiance and panel attitude

Table 5. PV-001 Test Case

| Case ID | PV-001 | Case Name | Solar irradiance and panel attitude |
| --- | --- | --- | --- |
| Test Objective | Verify how irradiance and panel orientation determine available power. Zero irradiance denotes full eclipse; a negative incidence cosine places the Sun behind the active face. Both must produce zero power. |  |  |
| Preconditions | Use the frozen section 5 inputs and environment; execute both implementations independently. Design basis: P2. |  |  |
| Input Data | All irradiances are crossed with seven incidence cosines. Python rotates the panel normal with a quaternion; Simulink receives the cosine of the same geometry. An analytical area times efficiency times front-face irradiance check is also applied. Exact values appear in the input table for this case. |  |  |
| Procedure | 1. Load this case and run the project model and Simulink independently. 2. Save outputs and events in input order or at the prescribed times. 3. Check validity, same-sample differences and case behavior; retain check records. |  |  |
| Expected Results | Rear illumination and eclipse yield zero power; other outputs equal active area times efficiency times front-face irradiance. |  |  |
| Acceptance Criteria | All applicable signals meet section 5.1 limits, flags and events match expectations, and the expected results in this form hold. |  |  |
| Case Designer |  | Executor / Date | Automated test 2026-10-07 |
| Actual Results | Completed 21 input combinations. Output availability, discrete status and applicable numerical difference checks pass. 42 checks recorded; evidence: results/PV-001.json. |  |  |
| Recorded By |  | Test Conclusion | [X] Pass [ ] Fail [ ] Not Executed |
| Anomalies | No anomaly against this case criteria. |  |  |

PV-001 Scenario Inputs and Initial Conditions

Table 6. PV-001 Scenario Inputs

| Index | G W/m² | cos θ |
| --- | --- | --- |
| 1 | 0 | −1 |
| 2 | 0 | −0.5 |
| 3 | 0 | 0 |
| 4 | 0 | 0.25 |
| 5 | 0 | 0.5 |
| 6 | 0 | 0.866025 |
| 7 | 0 | 1 |
| 8 | 680.5 | −1 |
| 9 | 680.5 | −0.5 |
| 10 | 680.5 | 0 |
| 11 | 680.5 | 0.25 |
| 12 | 680.5 | 0.5 |
| 13 | 680.5 | 0.866025 |
| 14 | 680.5 | 1 |
| 15 | 1361 | −1 |
| 16 | 1361 | −0.5 |
| 17 | 1361 | 0 |
| 18 | 1361 | 0.25 |
| 19 | 1361 | 0.5 |
| 20 | 1361 | 0.866025 |
| 21 | 1361 | 1 |

Parameters not overridden here use sections 5.2 and 6.1.

PV-001 Comparison Results

Figure 1  PV-001: Available solar power W. Top panels show both outputs at identical samples; lower panels show project model minus Simulink in the same units.

Horizontal indices match the input table for this case. Connecting lines aid reading and do not imply a dynamic trajectory between independent samples.

Table 7. PV-001 Numerical Errors and Limits

| Signal | Max absolute error | RMSE | Limit |
| --- | --- | --- | --- |
| Available solar power W | 4.55e−13 | 1.06e−13 | 1.00e−06 |
| State of charge fraction | 4.44e−16 | 4.44e−16 | 1.00e−06 |
| Battery temperature K | 0 | 0 | 0.001 |

Numerical comparison passes; overall acceptance: Pass. Recorded 42 checks.

Completed 21 input combinations. Output availability, discrete status and applicable numerical difference checks pass.

3.1.2 Test Project 2 Open circuit voltage and initial charge

Table 8. BT-001 Test Case

| Case ID | BT-001 | Case Name | Open circuit voltage and initial charge |
| --- | --- | --- | --- |
| Test Objective | Verify open circuit voltage at different initial charge levels. At zero cell current there is no charge transfer or current-induced heat; terminal voltage is the difference between electrode equilibrium potentials. |  |  |
| Preconditions | Use the frozen section 5 inputs and environment; execute both implementations independently. Design basis: P4–P8, P10. |  |  |
| Input Data | Sweep the negative-electrode mean fraction and derive the positive fraction from lithium inventory conservation. Temperature is 293.15 K or 20 degrees Celsius. The samples are independent states, not a charging trajectory. Exact values appear in the input table for this case. |  |  |
| Procedure | 1. Load this case and run the project model and Simulink independently. 2. Save outputs and events in input order or at the prescribed times. 3. Check validity, same-sample differences and case behavior; retain check records. |  |  |
| Expected Results | Zero current yields zero heat and fraction derivatives; terminal voltage equals the electrode equilibrium-potential difference. |  |  |
| Acceptance Criteria | All applicable signals meet section 5.1 limits, flags and events match expectations, and the expected results in this form hold. |  |  |
| Case Designer |  | Executor / Date | Automated test 2026-10-07 |
| Actual Results | Completed 9 input combinations. Output availability, discrete status and applicable numerical difference checks pass. 58 checks recorded; evidence: results/BT-001.json. |  |  |
| Recorded By |  | Test Conclusion | [X] Pass [ ] Fail [ ] Not Executed |
| Anomalies | No anomaly against this case criteria. |  |  |

BT-001 Scenario Inputs and Initial Conditions

Table 9. BT-001 Scenario Inputs

| Index | xn | xp | TB K | i A | Ns × Np |
| --- | --- | --- | --- | --- | --- |
| 1 | 0.1 | 0.773163 | 293.15 | 0 | 8 × 6 |
| 2 | 0.2 | 0.710267 | 293.15 | 0 | 8 × 6 |
| 3 | 0.3 | 0.647372 | 293.15 | 0 | 8 × 6 |
| 4 | 0.4 | 0.584477 | 293.15 | 0 | 8 × 6 |
| 5 | 0.5 | 0.521581 | 293.15 | 0 | 8 × 6 |
| 6 | 0.6 | 0.458686 | 293.15 | 0 | 8 × 6 |
| 7 | 0.7 | 0.395791 | 293.15 | 0 | 8 × 6 |
| 8 | 0.8 | 0.332895 | 293.15 | 0 | 8 × 6 |
| 9 | 0.88 | 0.282579 | 293.15 | 0 | 8 × 6 |

Parameters not overridden here use sections 5.2 and 6.1.

BT-001 Comparison Results

Figure 2  BT-001: Pack voltage V and State of charge fraction. Top panels show both outputs at identical samples; lower panels show project model minus Simulink in the same units.

Horizontal indices match the input table for this case. Connecting lines aid reading and do not imply a dynamic trajectory between independent samples.

Table 10. BT-001 Numerical Errors and Limits

| Signal | Max absolute error | RMSE | Limit |
| --- | --- | --- | --- |
| Pack voltage V | 4.62e−14 | 3.00e−14 | 1.00e−04 |
| State of charge fraction | 4.44e−16 | 2.88e−16 | 1.00e−06 |
| Pack current A | 0 | 0 | 1.00e−04 |
| Pack heat W | 0 | 0 | 1.00e−06 |
| Battery temperature K | 0 | 0 | 0.001 |

Numerical comparison passes; overall acceptance: Pass. Recorded 58 checks.

Completed 9 input combinations. Output availability, discrete status and applicable numerical difference checks pass.

3.1.3 Test Project 3 Charge and discharge voltage versus temperature

Table 11. BT-002 Test Case

| Case ID | BT-002 | Case Name | Charge and discharge voltage versus temperature |
| --- | --- | --- | --- |
| Test Objective | Verify charge and discharge voltage response and the effect of temperature on kinetics and diffusion. Positive current is discharge and negative current is charge. Temperature is the battery temperature, not ambient air in space. |  |  |
| Preconditions | Use the frozen section 5 inputs and environment; execute both implementations independently. Design basis: P4–P8, P10. |  |  |
| Input Data | Cross three cell temperatures with six cell currents at a common lithium state. Direct cell evaluation retains negative constraint margins for boundary diagnostics; not every sample is a feasible power-allocation operating point. Exact values appear in the input table for this case. |  |  |
| Procedure | 1. Load this case and run the project model and Simulink independently. 2. Save outputs and events in input order or at the prescribed times. 3. Check validity, same-sample differences and case behavior; retain check records. |  |  |
| Expected Results | Voltage, polarization and margins agree; infeasible current samples retain diagnostics and are not labeled feasible supply states. |  |  |
| Acceptance Criteria | All applicable signals meet section 5.1 limits, flags and events match expectations, and the expected results in this form hold. |  |  |
| Case Designer |  | Executor / Date | Automated test 2026-10-07 |
| Actual Results | Completed 18 input combinations. Output availability, discrete status and applicable numerical difference checks pass. 58 checks recorded; evidence: results/BT-002.json. |  |  |
| Recorded By |  | Test Conclusion | [X] Pass [ ] Fail [ ] Not Executed |
| Anomalies | No anomaly against this case criteria. |  |  |

BT-002 Scenario Inputs and Initial Conditions

Table 12. BT-002 Scenario Inputs

| Index | xn | xp | TB K | i A | Ns × Np |
| --- | --- | --- | --- | --- | --- |
| 1 | 0.6 | 0.458686 | 273.15 | −1 | 8 × 6 |
| 2 | 0.6 | 0.458686 | 273.15 | −0.5 | 8 × 6 |
| 3 | 0.6 | 0.458686 | 273.15 | 0 | 8 × 6 |
| 4 | 0.6 | 0.458686 | 273.15 | 0.5 | 8 × 6 |
| 5 | 0.6 | 0.458686 | 273.15 | 1 | 8 × 6 |
| 6 | 0.6 | 0.458686 | 273.15 | 2 | 8 × 6 |
| 7 | 0.6 | 0.458686 | 293.15 | −1 | 8 × 6 |
| 8 | 0.6 | 0.458686 | 293.15 | −0.5 | 8 × 6 |
| 9 | 0.6 | 0.458686 | 293.15 | 0 | 8 × 6 |
| 10 | 0.6 | 0.458686 | 293.15 | 0.5 | 8 × 6 |
| 11 | 0.6 | 0.458686 | 293.15 | 1 | 8 × 6 |
| 12 | 0.6 | 0.458686 | 293.15 | 2 | 8 × 6 |
| 13 | 0.6 | 0.458686 | 313.15 | −1 | 8 × 6 |
| 14 | 0.6 | 0.458686 | 313.15 | −0.5 | 8 × 6 |
| 15 | 0.6 | 0.458686 | 313.15 | 0 | 8 × 6 |
| 16 | 0.6 | 0.458686 | 313.15 | 0.5 | 8 × 6 |
| 17 | 0.6 | 0.458686 | 313.15 | 1 | 8 × 6 |
| 18 | 0.6 | 0.458686 | 313.15 | 2 | 8 × 6 |

Parameters not overridden here use sections 5.2 and 6.1.

BT-002 Comparison Results

Figure 3  BT-002: Pack voltage V and Pack current A. Top panels show both outputs at identical samples; lower panels show project model minus Simulink in the same units.

Horizontal indices match the input table for this case. Connecting lines aid reading and do not imply a dynamic trajectory between independent samples.

Table 13. BT-002 Numerical Errors and Limits

| Signal | Max absolute error | RMSE | Limit |
| --- | --- | --- | --- |
| Pack voltage V | 4.62e−14 | 2.26e−14 | 1.00e−04 |
| Pack current A | 0 | 0 | 1.00e−04 |
| Pack heat W | 3.20e−14 | 7.78e−15 | 1.00e−06 |
| State of charge fraction | 4.44e−16 | 4.44e−16 | 1.00e−06 |
| Battery temperature K | 0 | 0 | 0.001 |

Numerical comparison passes; overall acceptance: Pass. Recorded 58 checks.

Completed 18 input combinations. Output availability, discrete status and applicable numerical difference checks pass.

3.1.4 Test Project 4 Battery heat and reversible heat sign

Table 14. BT-003 Test Case

| Case ID | BT-003 | Case Name | Battery heat and reversible heat sign |
| --- | --- | --- | --- |
| Test Objective | Verify reaction heat, ohmic heat and signed reversible heat. Reversible heat can make total heat negative at low current; this denotes net heat absorption in the model and must not be clipped to zero. |  |  |
| Preconditions | Use the frozen section 5 inputs and environment; execute both implementations independently. Design basis: P4–P8, P10. |  |  |
| Input Data | Hold both lithium fractions fixed and scan small positive and negative currents at 283.15 K and 303.15 K. Compare pack heat and cell reversible heat separately. Exact values appear in the input table for this case. |  |  |
| Procedure | 1. Load this case and run the project model and Simulink independently. 2. Save outputs and events in input order or at the prescribed times. 3. Check validity, same-sample differences and case behavior; retain check records. |  |  |
| Expected Results | Reaction, ohmic and reversible heat sum consistently; negative reversible heat and total heat are retained. |  |  |
| Acceptance Criteria | All applicable signals meet section 5.1 limits, flags and events match expectations, and the expected results in this form hold. |  |  |
| Case Designer |  | Executor / Date | Automated test 2026-10-07 |
| Actual Results | Pack heat ranges from −0.0320434 to 3.23576 W; negative heat is retained. 60 checks recorded; evidence: results/BT-003.json. |  |  |
| Recorded By |  | Test Conclusion | [X] Pass [ ] Fail [ ] Not Executed |
| Anomalies | No anomaly against this case criteria. |  |  |

BT-003 Scenario Inputs and Initial Conditions

Table 15. BT-003 Scenario Inputs

| Index | xn | xp | TB K | i A | Ns × Np |
| --- | --- | --- | --- | --- | --- |
| 1 | 0.6 | 0.458686 | 283.15 | −0.5 | 8 × 6 |
| 2 | 0.6 | 0.458686 | 283.15 | −0.1 | 8 × 6 |
| 3 | 0.6 | 0.458686 | 283.15 | 0 | 8 × 6 |
| 4 | 0.6 | 0.458686 | 283.15 | 0.1 | 8 × 6 |
| 5 | 0.6 | 0.458686 | 283.15 | 0.5 | 8 × 6 |
| 6 | 0.6 | 0.458686 | 283.15 | 1 | 8 × 6 |
| 7 | 0.6 | 0.458686 | 303.15 | −0.5 | 8 × 6 |
| 8 | 0.6 | 0.458686 | 303.15 | −0.1 | 8 × 6 |
| 9 | 0.6 | 0.458686 | 303.15 | 0 | 8 × 6 |
| 10 | 0.6 | 0.458686 | 303.15 | 0.1 | 8 × 6 |
| 11 | 0.6 | 0.458686 | 303.15 | 0.5 | 8 × 6 |
| 12 | 0.6 | 0.458686 | 303.15 | 1 | 8 × 6 |

Parameters not overridden here use sections 5.2 and 6.1.

BT-003 Comparison Results

Figure 4  BT-003: Pack heat W and Cell reversible heat W. Top panels show both outputs at identical samples; lower panels show project model minus Simulink in the same units.

Horizontal indices match the input table for this case. Connecting lines aid reading and do not imply a dynamic trajectory between independent samples.

Table 16. BT-003 Numerical Errors and Limits

| Signal | Max absolute error | RMSE | Limit |
| --- | --- | --- | --- |
| Pack heat W | 4.44e−15 | 1.73e−15 | 1.00e−06 |
| Cell reversible heat W | 3.12e−17 | 1.19e−17 | 1.00e−06 |
| Pack voltage V | 4.26e−14 | 2.32e−14 | 1.00e−04 |
| Pack current A | 1.11e−16 | 6.41e−17 | 1.00e−04 |
| State of charge fraction | 4.44e−16 | 4.44e−16 | 1.00e−06 |
| Battery temperature K | 0 | 0 | 0.001 |

Numerical comparison passes; overall acceptance: Pass. Recorded 60 checks.

Pack heat ranges from −0.0320434 to 3.23576 W; negative heat is retained.

3.1.5 Test Project 5 Cell to series and parallel pack scaling

Table 17. BT-004 Test Case

| Case ID | BT-004 | Case Name | Cell to series and parallel pack scaling |
| --- | --- | --- | --- |
| Test Objective | Verify cell-to-pack conversion. Series count scales pack voltage, parallel count scales pack current, and their product scales pack power and heat. Scaling must be applied once. |  |  |
| Preconditions | Use the frozen section 5 inputs and environment; execute both implementations independently. Design basis: P4–P8, P10. |  |  |
| Input Data | Five series and parallel configurations share the same cell state, 0.5 A cell discharge current and 293.15 K temperature. Cells have identical states and temperature, with equal parallel current sharing. Exact values appear in the input table for this case. |  |  |
| Procedure | 1. Load this case and run the project model and Simulink independently. 2. Save outputs and events in input order or at the prescribed times. 3. Check validity, same-sample differences and case behavior; retain check records. |  |  |
| Expected Results | Pack voltage scales with series count, current with parallel count, and power and heat with total cell count. |  |  |
| Acceptance Criteria | All applicable signals meet section 5.1 limits, flags and events match expectations, and the expected results in this form hold. |  |  |
| Case Designer |  | Executor / Date | Automated test 2026-10-07 |
| Actual Results | Completed 5 input combinations. Output availability, discrete status and applicable numerical difference checks pass. 58 checks recorded; evidence: results/BT-004.json. |  |  |
| Recorded By |  | Test Conclusion | [X] Pass [ ] Fail [ ] Not Executed |
| Anomalies | No anomaly against this case criteria. |  |  |

BT-004 Scenario Inputs and Initial Conditions

Table 18. BT-004 Scenario Inputs

| Index | xn | xp | TB K | i A | Ns × Np |
| --- | --- | --- | --- | --- | --- |
| 1 | 0.6 | 0.458686 | 293.15 | 0.5 | 1 × 1 |
| 2 | 0.6 | 0.458686 | 293.15 | 0.5 | 8 × 1 |
| 3 | 0.6 | 0.458686 | 293.15 | 0.5 | 1 × 6 |
| 4 | 0.6 | 0.458686 | 293.15 | 0.5 | 8 × 6 |
| 5 | 0.6 | 0.458686 | 293.15 | 0.5 | 12 × 4 |

Parameters not overridden here use sections 5.2 and 6.1.

BT-004 Comparison Results

Figure 5  BT-004: Pack voltage V and Pack current A. Top panels show both outputs at identical samples; lower panels show project model minus Simulink in the same units.

Horizontal indices match the input table for this case. Connecting lines aid reading and do not imply a dynamic trajectory between independent samples.

Table 19. BT-004 Numerical Errors and Limits

| Signal | Max absolute error | RMSE | Limit |
| --- | --- | --- | --- |
| Pack voltage V | 3.20e−14 | 2.05e−14 | 1.00e−04 |
| Pack current A | 0 | 0 | 1.00e−04 |
| Pack heat W | 3.33e−16 | 2.46e−16 | 1.00e−06 |
| State of charge fraction | 4.44e−16 | 4.44e−16 | 1.00e−06 |
| Battery temperature K | 0 | 0 | 0.001 |

Numerical comparison passes; overall acceptance: Pass. Recorded 58 checks.

Completed 5 input combinations. Output availability, discrete status and applicable numerical difference checks pass.

3.2 Power Allocation and Protection Interfaces

3.2.1 Test Project 6 Solar and battery power allocation

Table 20. PD-001 Test Case

| Case ID | PD-001 | Case Name | Solar and battery power allocation |
| --- | --- | --- | --- |
| Test Objective | Verify power allocation among array, battery and load. Surplus solar charges the battery; a deficit calls for battery discharge. A request beyond the allowed battery capability must report supply shortfall. |  |  |
| Preconditions | Use the frozen section 5 inputs and environment; execute both implementations independently. Design basis: P1, P3, P11. |  |  |
| Input Data | Cross four irradiances with six load requests. Distribution efficiency is 0.95, so bus-side demand exceeds load demand. Shortfall samples compare status flags and must not publish artificial zero heat as a valid result. Exact values appear in the input table for this case. |  |  |
| Procedure | 1. Load this case and run the project model and Simulink independently. 2. Save outputs and events in input order or at the prescribed times. 3. Check validity, same-sample differences and case behavior; retain check records. |  |  |
| Expected Results | Surplus solar charges the battery; a deficit discharges it; infeasible requests explicitly report shortfall. |  |  |
| Acceptance Criteria | All applicable signals meet section 5.1 limits, flags and events match expectations, and the expected results in this form hold. |  |  |
| Case Designer |  | Executor / Date | Automated test 2026-10-07 |
| Actual Results | Completed 24 input combinations. Output availability, discrete status and applicable numerical difference checks pass. 57 checks recorded; evidence: results/PD-001.json. |  |  |
| Recorded By |  | Test Conclusion | [X] Pass [ ] Fail [ ] Not Executed |
| Anomalies | No anomaly against this case criteria. |  |  |

PD-001 Scenario Inputs and Initial Conditions

Table 21. PD-001 Scenario Inputs

| Index | G W/m² | Demand W | TB K | Override |
| --- | --- | --- | --- | --- |
| 1 | 0 | 0 | 293.15 | Baseline |
| 2 | 0 | 50 | 293.15 | Baseline |
| 3 | 0 | 200 | 293.15 | Baseline |
| 4 | 0 | 400 | 293.15 | Baseline |
| 5 | 0 | 900 | 293.15 | Baseline |
| 6 | 0 | 2500 | 293.15 | Baseline |
| 7 | 300 | 0 | 293.15 | Baseline |
| 8 | 300 | 50 | 293.15 | Baseline |
| 9 | 300 | 200 | 293.15 | Baseline |
| 10 | 300 | 400 | 293.15 | Baseline |
| 11 | 300 | 900 | 293.15 | Baseline |
| 12 | 300 | 2500 | 293.15 | Baseline |
| 13 | 800 | 0 | 293.15 | Baseline |
| 14 | 800 | 50 | 293.15 | Baseline |
| 15 | 800 | 200 | 293.15 | Baseline |
| 16 | 800 | 400 | 293.15 | Baseline |
| 17 | 800 | 900 | 293.15 | Baseline |
| 18 | 800 | 2500 | 293.15 | Baseline |
| 19 | 1361 | 0 | 293.15 | Baseline |
| 20 | 1361 | 50 | 293.15 | Baseline |
| 21 | 1361 | 200 | 293.15 | Baseline |
| 22 | 1361 | 400 | 293.15 | Baseline |
| 23 | 1361 | 900 | 293.15 | Baseline |
| 24 | 1361 | 2500 | 293.15 | Baseline |

Parameters not overridden here use sections 5.2 and 6.1.

PD-001 Comparison Results

Figure 6  PD-001: Delivered load power W and Pack current A. Top panels show both outputs at identical samples; lower panels show project model minus Simulink in the same units.

Horizontal indices match the input table for this case. Connecting lines aid reading and do not imply a dynamic trajectory between independent samples.

Table 22. PD-001 Numerical Errors and Limits

| Signal | Max absolute error | RMSE | Limit |
| --- | --- | --- | --- |
| Delivered load power W | 1.78e−13 | 5.86e−14 | 1.00e−06 |
| Pack current A | 8.43e−12 | 3.23e−12 | 1.00e−04 |
| Actual solar power W | 2.85e−10 | 1.07e−10 | 1.00e−06 |
| Pack voltage V | 5.97e−13 | 2.46e−13 | 1.00e−04 |
| Pack heat W | 1.58e−11 | 4.70e−12 | 1.00e−06 |
| State of charge fraction | 4.44e−16 | 4.44e−16 | 1.00e−06 |
| Battery temperature K | 0 | 0 | 0.001 |

Numerical comparison passes; overall acceptance: Pass. Recorded 57 checks.

Completed 24 input combinations. Output availability, discrete status and applicable numerical difference checks pass.

3.2.2 Test Project 7 Distribution efficiency and loss

Table 23. PD-002 Test Case

| Case ID | PD-002 | Case Name | Distribution efficiency and loss |
| --- | --- | --- | --- |
| Test Objective | Verify that distribution input splits into load power and distribution heat, with no omitted or double-counted loss. |  |  |
| Preconditions | Use the frozen section 5 inputs and environment; execute both implementations independently. Design basis: P1, P3, P11. |  |  |
| Input Data | Set solar input to zero and supply the load from the battery at efficiencies 0.80, 0.95 and 1.00. The ideal 1.00 boundary must have zero distribution heat. Exact values appear in the input table for this case. |  |  |
| Procedure | 1. Load this case and run the project model and Simulink independently. 2. Save outputs and events in input order or at the prescribed times. 3. Check validity, same-sample differences and case behavior; retain check records. |  |  |
| Expected Results | Load plus distribution heat equals distribution input; unit efficiency produces zero distribution heat. |  |  |
| Acceptance Criteria | All applicable signals meet section 5.1 limits, flags and events match expectations, and the expected results in this form hold. |  |  |
| Case Designer |  | Executor / Date | Automated test 2026-10-07 |
| Actual Results | Completed 9 input combinations. Output availability, discrete status and applicable numerical difference checks pass. 57 checks recorded; evidence: results/PD-002.json. |  |  |
| Recorded By |  | Test Conclusion | [X] Pass [ ] Fail [ ] Not Executed |
| Anomalies | No anomaly against this case criteria. |  |  |

PD-002 Scenario Inputs and Initial Conditions

Table 24. PD-002 Scenario Inputs

| Index | G W/m² | Demand W | TB K | Override |
| --- | --- | --- | --- | --- |
| 1 | 0 | 0 | 293.15 | eta=0.8 |
| 2 | 0 | 100 | 293.15 | eta=0.8 |
| 3 | 0 | 300 | 293.15 | eta=0.8 |
| 4 | 0 | 0 | 293.15 | eta=0.95 |
| 5 | 0 | 100 | 293.15 | eta=0.95 |
| 6 | 0 | 300 | 293.15 | eta=0.95 |
| 7 | 0 | 0 | 293.15 | eta=1 |
| 8 | 0 | 100 | 293.15 | eta=1 |
| 9 | 0 | 300 | 293.15 | eta=1 |

Parameters not overridden here use sections 5.2 and 6.1.

PD-002 Comparison Results

Figure 7  PD-002: Delivered load power W and Distribution loss W. Top panels show both outputs at identical samples; lower panels show project model minus Simulink in the same units.

Horizontal indices match the input table for this case. Connecting lines aid reading and do not imply a dynamic trajectory between independent samples.

Table 25. PD-002 Numerical Errors and Limits

| Signal | Max absolute error | RMSE | Limit |
| --- | --- | --- | --- |
| Delivered load power W | 1.08e−12 | 3.65e−13 | 1.00e−06 |
| Distribution loss W | 2.98e−13 | 1.02e−13 | 1.00e−06 |
| Actual solar power W | 0 | 0 | 1.00e−06 |
| Pack voltage V | 4.26e−14 | 2.15e−14 | 1.00e−04 |
| Pack current A | 4.44e−14 | 1.68e−14 | 1.00e−04 |
| Pack heat W | 4.62e−14 | 1.55e−14 | 1.00e−06 |
| State of charge fraction | 4.44e−16 | 4.44e−16 | 1.00e−06 |
| Battery temperature K | 0 | 0 | 0.001 |

Numerical comparison passes; overall acceptance: Pass. Recorded 57 checks.

Completed 9 input combinations. Output availability, discrete status and applicable numerical difference checks pass.

3.2.3 Test Project 8 Charge limits and solar curtailment

Table 26. CT-001 Test Case

| Case ID | CT-001 | Case Name | Charge limits and solar curtailment |
| --- | --- | --- | --- |
| Test Objective | Verify curtailment when solar surplus exceeds the battery charge capability. Current, voltage and particle center or surface fractions can constrain charging. |  |  |
| Preconditions | Use the frozen section 5 inputs and environment; execute both implementations independently. Design basis: P1, P3, P11. |  |  |
| Input Data | Use an artificial 1800 W/m² irradiance and a 25 W load to guarantee surplus. This is a boundary stress test, not a solar constant assigned to a real orbit. Tighten charge current or voltage limits, or lower battery temperature. Exact values appear in the input table for this case. |  |  |
| Procedure | 1. Load this case and run the project model and Simulink independently. 2. Save outputs and events in input order or at the prescribed times. 3. Check validity, same-sample differences and case behavior; retain check records. |  |  |
| Expected Results | Honor charge limits and curtail solar while satisfying feasible load and terminal-power conservation. |  |  |
| Acceptance Criteria | All applicable signals meet section 5.1 limits, flags and events match expectations, and the expected results in this form hold. |  |  |
| Case Designer |  | Executor / Date | Automated test 2026-10-07 |
| Actual Results | Completed 6 input combinations. Output availability, discrete status and applicable numerical difference checks pass. 57 checks recorded; evidence: results/CT-001.json. |  |  |
| Recorded By |  | Test Conclusion | [X] Pass [ ] Fail [ ] Not Executed |
| Anomalies | No anomaly against this case criteria. |  |  |

CT-001 Scenario Inputs and Initial Conditions

Table 27. CT-001 Scenario Inputs

| Index | G W/m² | Demand W | TB K | Override |
| --- | --- | --- | --- | --- |
| 1 | 1800 | 25 | 293.15 | imin=−0.2 |
| 2 | 1800 | 25 | 293.15 | vmax=4.03 |
| 3 | 1800 | 25 | 253.15 | Baseline |
| 4 | 1800 | 25 | 273.15 | Baseline |
| 5 | 1800 | 25 | 313.15 | Baseline |
| 6 | 1800 | 25 | 293.15 | Baseline |

Parameters not overridden here use sections 5.2 and 6.1.

CT-001 Comparison Results

Figure 8  CT-001: Actual solar power W and Cell current A. Top panels show both outputs at identical samples; lower panels show project model minus Simulink in the same units.

Horizontal indices match the input table for this case. Connecting lines aid reading and do not imply a dynamic trajectory between independent samples.

Table 28. CT-001 Numerical Errors and Limits

| Signal | Max absolute error | RMSE | Limit |
| --- | --- | --- | --- |
| Actual solar power W | 1.90e−10 | 9.97e−11 | 1.00e−06 |
| Cell current A | 9.58e−13 | 4.90e−13 | 1.00e−04 |
| Delivered load power W | 0 | 0 | 1.00e−06 |
| Pack voltage V | 7.60e−13 | 3.59e−13 | 1.00e−04 |
| Pack current A | 5.75e−12 | 2.94e−12 | 1.00e−04 |
| Pack heat W | 1.02e−11 | 5.30e−12 | 1.00e−06 |
| State of charge fraction | 4.44e−16 | 4.44e−16 | 1.00e−06 |
| Battery temperature K | 0 | 0 | 0.001 |

Numerical comparison passes; overall acceptance: Pass. Recorded 57 checks.

Completed 6 input combinations. Output availability, discrete status and applicable numerical difference checks pass.

3.2.4 Test Project 9 Discharge capability and supply shortfall

Table 29. CT-002 Test Case

| Case ID | CT-002 | Case Name | Discharge capability and supply shortfall |
| --- | --- | --- | --- |
| Test Objective | Verify discharge limits and supply shortfall classification. A physically infeasible request must request an event and must not be mislabeled as a numerical solver failure. |  |  |
| Preconditions | Use the frozen section 5 inputs and environment; execute both implementations independently. Design basis: P1, P3, P11. |  |  |
| Input Data | With no solar input, cross three requests with four battery settings: baseline, reduced discharge current, higher minimum voltage and low temperature. Each sample solves its own allowed current interval. Exact values appear in the input table for this case. |  |  |
| Procedure | 1. Load this case and run the project model and Simulink independently. 2. Save outputs and events in input order or at the prescribed times. 3. Check validity, same-sample differences and case behavior; retain check records. |  |  |
| Expected Results | Infeasible demand returns shortfall and an event request, distinguished from numerical failure. |  |  |
| Acceptance Criteria | All applicable signals meet section 5.1 limits, flags and events match expectations, and the expected results in this form hold. |  |  |
| Case Designer |  | Executor / Date | Automated test 2026-10-07 |
| Actual Results | Completed 12 input combinations. Output availability, discrete status and applicable numerical difference checks pass. 57 checks recorded; evidence: results/CT-002.json. |  |  |
| Recorded By |  | Test Conclusion | [X] Pass [ ] Fail [ ] Not Executed |
| Anomalies | No anomaly against this case criteria. |  |  |

CT-002 Scenario Inputs and Initial Conditions

Table 30. CT-002 Scenario Inputs

| Index | G W/m² | Demand W | TB K | Override |
| --- | --- | --- | --- | --- |
| 1 | 0 | 20 | 293.15 | Baseline |
| 2 | 0 | 100 | 293.15 | Baseline |
| 3 | 0 | 1000 | 293.15 | Baseline |
| 4 | 0 | 20 | 293.15 | imax=0.25 |
| 5 | 0 | 100 | 293.15 | imax=0.25 |
| 6 | 0 | 1000 | 293.15 | imax=0.25 |
| 7 | 0 | 20 | 293.15 | vmin=3.9 |
| 8 | 0 | 100 | 293.15 | vmin=3.9 |
| 9 | 0 | 1000 | 293.15 | vmin=3.9 |
| 10 | 0 | 20 | 253.15 | Baseline |
| 11 | 0 | 100 | 253.15 | Baseline |
| 12 | 0 | 1000 | 253.15 | Baseline |

Parameters not overridden here use sections 5.2 and 6.1.

CT-002 Comparison Results

Figure 9  CT-002: Supply capability flag and Event required flag. Top panels show both outputs at identical samples; lower panels show project model minus Simulink in the same units.

Horizontal indices match the input table for this case. Connecting lines aid reading and do not imply a dynamic trajectory between independent samples.

Table 31. CT-002 Numerical Errors and Limits

| Signal | Max absolute error | RMSE | Limit |
| --- | --- | --- | --- |
| Supply capability flag | 0 | 0 | 0 |
| Event required flag | 0 | 0 | 0 |
| Actual solar power W | 0 | 0 | 1.00e−06 |
| Delivered load power W | 1.11e−10 | 4.52e−11 | 1.00e−06 |
| Pack voltage V | 2.59e−13 | 1.11e−13 | 1.00e−04 |
| Pack current A | 3.74e−12 | 1.53e−12 | 1.00e−04 |
| Pack heat W | 6.34e−13 | 2.59e−13 | 1.00e−06 |
| State of charge fraction | 4.44e−16 | 4.44e−16 | 1.00e−06 |

Numerical comparison passes; overall acceptance: Pass. Recorded 57 checks.

Completed 12 input combinations. Output availability, discrete status and applicable numerical difference checks pass.

3.2.5 Test Project 10 Charging boundary at full state of charge

Table 32. CT-003 Test Case

| Case ID | CT-003 | Case Name | Charging boundary at full state of charge |
| --- | --- | --- | --- |
| Test Objective | Verify the design requirement to limit charging at full charge. The configured 100% SOC point is negative fraction 0.90 and positive fraction 0.27. Solar surplus at this state should not continue charging the battery. |  |  |
| Preconditions | Use the frozen section 5 inputs and environment; execute both implementations independently. Design basis: P1, P3, P11. |  |  |
| Input Data | Set initial SOC to 1, request 25 W, and apply three irradiances. Coverage review added this case after orbital runs exceeded SOC 1; the original numerical comparison tolerances were not relaxed. Exact values appear in the input table for this case. |  |  |
| Procedure | 1. Load this case and run the project model and Simulink independently. 2. Save outputs and events in input order or at the prescribed times. 3. Check validity, same-sample differences and case behavior; retain check records. |  |  |
| Expected Results | At SOC one, stop further charging and curtail surplus solar. |  |  |
| Acceptance Criteria | All applicable signals meet section 5.1 limits, flags and events match expectations, and the expected results in this form hold. |  |  |
| Case Designer |  | Executor / Date | Automated test 2026-10-07 |
| Actual Results | All three full-charge samples continue charging, with minimum cell current −0.544984 A. Numerical agreement passes, but the full-charge requirement fails. 59 checks recorded; evidence: results/CT-003.json. |  |  |
| Recorded By |  | Test Conclusion | [ ] Pass [X] Fail [ ] Not Executed |
| Anomalies | All three full-charge samples continue charging, with minimum cell current −0.544984 A. Numerical agreement passes, but the full-charge requirement fails. |  |  |

CT-003 Scenario Inputs and Initial Conditions

Table 33. CT-003 Scenario Inputs

| Index | G W/m² | Demand W | TB K | Override |
| --- | --- | --- | --- | --- |
| 1 | 800 | 25 | 293.15 | Baseline |
| 2 | 1361 | 25 | 293.15 | Baseline |
| 3 | 1800 | 25 | 293.15 | Baseline |

xn = 0.90; xp = 0.27; SOC = 1; cos θ = 1.

Parameters not overridden here use sections 5.2 and 6.1.

CT-003 Comparison Results

Figure 10  CT-003: Cell current A and Actual solar power W. Top panels show both outputs at identical samples; lower panels show project model minus Simulink in the same units.

Horizontal indices match the input table for this case. Connecting lines aid reading and do not imply a dynamic trajectory between independent samples.

Table 34. CT-003 Numerical Errors and Limits

| Signal | Max absolute error | RMSE | Limit |
| --- | --- | --- | --- |
| Cell current A | 5.46e−13 | 5.46e−13 | 1.00e−04 |
| Actual solar power W | 1.11e−10 | 1.11e−10 | 1.00e−06 |
| Delivered load power W | 0 | 0 | 1.00e−06 |
| Pack voltage V | 2.98e−13 | 2.98e−13 | 1.00e−04 |
| Pack current A | 3.27e−12 | 3.27e−12 | 1.00e−04 |
| Pack heat W | 1.48e−12 | 1.48e−12 | 1.00e−06 |
| State of charge fraction | 0 | 0 | 1.00e−06 |
| Battery temperature K | 0 | 0 | 0.001 |

Numerical comparison passes; overall acceptance: Fail. Recorded 59 checks.

All three full-charge samples continue charging, with minimum cell current −0.544984 A. Numerical agreement passes, but the full-charge requirement fails.

3.2.6 Test Project 11 Protection commands and latched states

Table 35. PR-001 Test Case

| Case ID | PR-001 | Case Name | Protection commands and latched states |
| --- | --- | --- | --- |
| Test Objective | Verify start and stop commands, loss-of-supply latching, denied restart, simultaneous command priority and duplicate commands. Restored sunlight alone must not restart a latched load. |  |  |
| Preconditions | Use the frozen section 5 inputs and environment; execute both implementations independently. Design basis: 5. |  |  |
| Input Data | Eight configurations cover stop, feasible and infeasible start, supply loss, simultaneous stop and start, duplicate stop, and an unaccepted trial event. A trial event must be rejected without changing state. Exact values appear in the input table for this case. |  |  |
| Procedure | 1. Load this case and run the project model and Simulink independently. 2. Save outputs and events in input order or at the prescribed times. 3. Check validity, same-sample differences and case behavior; retain check records. |  |  |
| Expected Results | Start, stop, latching, command priority and trial-event rejection match the prescribed event sequence. |  |  |
| Acceptance Criteria | All applicable signals meet section 5.1 limits, flags and events match expectations, and the expected results in this form hold. |  |  |
| Case Designer |  | Executor / Date | Automated test 2026-10-07 |
| Actual Results | Completed 8 input combinations. Output availability, discrete status and applicable numerical difference checks pass. 59 checks recorded; evidence: results/PR-001.json. |  |  |
| Recorded By |  | Test Conclusion | [X] Pass [ ] Fail [ ] Not Executed |
| Anomalies | No anomaly against this case criteria. |  |  |

PR-001 Scenario Inputs and Initial Conditions

Table 36. PR-001 Scenario Inputs

| Index | G W/m² | Demand W | Connected / latched | Command |
| --- | --- | --- | --- | --- |
| 1 | 1361 | 200 | 1 / 0 | stop |
| 2 | 1361 | 200 | 0 / 0 | start |
| 3 | 0 | 2500 | 0 / 1 | start |
| 4 | 1361 | 200 | 0 / 1 | start |
| 5 | 0 | 2500 | 1 / 0 | supply_loss |
| 6 | 1361 | 200 | 1 / 0 | stop_start |
| 7 | 1361 | 200 | 1 / 0 | repeat_stop |
| 8 | 0 | 2500 | 1 / 0 | trial_supply_loss |

Parameters not overridden here use sections 5.2 and 6.1.

PR-001 Comparison Results

Figure 11  PR-001: Load connected flag and Supply trip latched flag. Top panels show both outputs at identical samples; lower panels show project model minus Simulink in the same units.

Horizontal indices match the input table for this case. Connecting lines aid reading and do not imply a dynamic trajectory between independent samples.

Table 37. PR-001 Numerical Errors and Limits

| Signal | Max absolute error | RMSE | Limit |
| --- | --- | --- | --- |
| Load connected flag | 0 | 0 | 0 |
| Supply trip latched flag | 0 | 0 | 0 |
| Actual solar power W | 2.85e−10 | 1.52e−10 | 1.00e−06 |
| Delivered load power W | 0 | 0 | 1.00e−06 |
| Pack voltage V | 5.97e−13 | 3.19e−13 | 1.00e−04 |
| Pack current A | 8.43e−12 | 4.51e−12 | 1.00e−04 |
| Pack heat W | 1.58e−11 | 8.45e−12 | 1.00e−06 |
| State of charge fraction | 4.44e−16 | 4.44e−16 | 1.00e−06 |

Numerical comparison passes; overall acceptance: Pass. Recorded 59 checks.

Completed 8 input combinations. Output availability, discrete status and applicable numerical difference checks pass.

3.2.7 Test Project 12 Invalid inputs and state boundaries

Table 38. IV-001 Test Case

| Case ID | IV-001 | Case Name | Invalid inputs and state boundaries |
| --- | --- | --- | --- |
| Test Objective | Distinguish invalid input from a physical state boundary. Invalid input must not drive protection; a trial state outside material limits must report a device boundary requiring handling. |  |  |
| Preconditions | Use the frozen section 5 inputs and environment; execute both implementations independently. Design basis: 5. |  |  |
| Input Data | Test 240 K battery temperature, mismatched run identity, mismatched time, unsupported frame, zero Sun direction and an out-of-range mean lithium fraction. The first five are invalid; the last is a valid boundary-event report. Exact values appear in the input table for this case. |  |  |
| Procedure | 1. Load this case and run the project model and Simulink independently. 2. Save outputs and events in input order or at the prescribed times. 3. Check validity, same-sample differences and case behavior; retain check records. |  |  |
| Expected Results | The first five inputs are invalid; the sixth is a valid device-boundary event. Invalid results do not fabricate port values. |  |  |
| Acceptance Criteria | All applicable signals meet section 5.1 limits, flags and events match expectations, and the expected results in this form hold. |  |  |
| Case Designer |  | Executor / Date | Automated test 2026-10-07 |
| Actual Results | Completed 6 input combinations. Output availability, discrete status and applicable numerical difference checks pass. 40 checks recorded; evidence: results/IV-001.json. |  |  |
| Recorded By |  | Test Conclusion | [X] Pass [ ] Fail [ ] Not Executed |
| Anomalies | No anomaly against this case criteria. |  |  |

IV-001 Scenario Inputs and Initial Conditions

Table 39. IV-001 Scenario Inputs

| Index | Input change | Expected class |
| --- | --- | --- |
| 1 | temperature | Invalid input |
| 2 | identity | Invalid input |
| 3 | time | Invalid input |
| 4 | frame | Invalid input |
| 5 | zero_sun | Invalid input |
| 6 | mean_boundary | Boundary event |

Parameters not overridden here use sections 5.2 and 6.1.

IV-001 Comparison Results

Figure 12  IV-001: Valid flag and Event required flag. Top panels show both outputs at identical samples; lower panels show project model minus Simulink in the same units.

Horizontal indices match the input table for this case. Connecting lines aid reading and do not imply a dynamic trajectory between independent samples.

Table 40. IV-001 Numerical Errors and Limits

| Signal | Max absolute error | RMSE | Limit |
| --- | --- | --- | --- |
| Valid flag | 0 | 0 | 0 |
| Event required flag | 0 | 0 | 0 |
| State of charge fraction | 4.44e−16 | 4.44e−16 | 1.00e−06 |

Numerical comparison passes; overall acceptance: Pass. Recorded 40 checks.

Completed 6 input combinations. Output availability, discrete status and applicable numerical difference checks pass.

3.3 Dynamic Supply and Electrothermal Processes

3.3.1 Test Project 13 Charging under continuous sunlight

Table 41. DY-001 Test Case

| Case ID | DY-001 | Case Name | Charging under continuous sunlight |
| --- | --- | --- | --- |
| Test Objective | Verify gradual charging in continuous sunlight and agreement of SOC, current, voltage and heat between the independent integrators. |  |  |
| Preconditions | Use the frozen section 5 inputs and environment; execute both implementations independently. Design basis: P1–P11. |  |  |
| Input Data | Normal solar incidence at 1361 W/m², a 200 W load and a prescribed 293.15 K battery temperature for 900 s. Save results every 10 s. Exact values appear in the input table for this case. |  |  |
| Procedure | 1. Load this case and run the project model and Simulink independently. 2. Save outputs and events in input order or at the prescribed times. 3. Check validity, same-sample differences and case behavior; retain check records. |  |  |
| Expected Results | SOC rises continuously within zero to one, power is conserved, and dynamic outputs agree within tolerance. |  |  |
| Acceptance Criteria | All applicable signals meet section 5.1 limits, flags and events match expectations, and the expected results in this form hold. |  |  |
| Case Designer |  | Executor / Date | Automated test 2026-10-07 |
| Actual Results | SOC changes from 65.517% to 88.654%; battery temperature changes from 293.150 K to 293.150 K. 87 checks recorded; evidence: results/DY-001.json. |  |  |
| Recorded By |  | Test Conclusion | [X] Pass [ ] Fail [ ] Not Executed |
| Anomalies | No anomaly against this case criteria. |  |  |

DY-001 Scenario Inputs and Initial Conditions

Table 42. DY-001 Scenario Inputs

| Time s | G W/m² | Demand W | Start command |
| --- | --- | --- | --- |
| 0 to 900 | 1361 | 200 | none |

Initial xn = 0.60, xp = 0.458686001; initial temperature 293.15 K; incidence cosine 1; output interval 10 s.

Parameters not overridden here use sections 5.2 and 6.1.

DY-001 Comparison Results

Figure 13  DY-001: State of charge fraction and Pack current A. Top panels show both outputs at identical samples; lower panels show project model minus Simulink in the same units.

The horizontal axis is minutes. Vertical changes retain both sides of a discontinuity at the same time; no interpolation spans that discontinuity.

Table 43. DY-001 Numerical Errors and Limits

| Signal | Max absolute error | RMSE | Limit |
| --- | --- | --- | --- |
| State of charge fraction | 4.78e−08 | 2.03e−08 | 1.00e−06 |
| Pack current A | 3.75e−06 | 1.58e−06 | 1.00e−04 |
| Actual solar power W | 1.26e−04 | 5.32e−05 | 0.001 |
| Delivered load power W | 0 | 0 | 0.001 |
| Pack voltage V | 1.57e−12 | 7.88e−13 | 1.00e−04 |
| Pack heat W | 6.81e−06 | 2.61e−06 | 0.001 |
| Battery temperature K | 0 | 0 | 0.001 |

Numerical comparison passes; overall acceptance: Pass. Recorded 87 checks.

SOC changes from 65.517% to 88.654%; battery temperature changes from 293.150 K to 293.150 K.

3.3.2 Test Project 14 Eclipse entry and exit

Table 44. DY-002 Test Case

| Case ID | DY-002 | Case Name | Eclipse entry and exit |
| --- | --- | --- | --- |
| Test Objective | Verify transitions from sunlight into eclipse and back. Solar output is zero in eclipse and the battery supplies the load; sunlight recovery restores array power and possible charging. |  |  |
| Preconditions | Use the frozen section 5 inputs and environment; execute both implementations independently. Design basis: P1–P11. |  |  |
| Input Data | Use a controlled 5400 s cycle with full eclipse from 1800 to 3800 s and 1361 W/m² otherwise. Load stays at 200 W. This fixture is neither ISS telemetry nor orbit-propagator output. Exact values appear in the input table for this case. |  |  |
| Procedure | 1. Load this case and run the project model and Simulink independently. 2. Save outputs and events in input order or at the prescribed times. 3. Check validity, same-sample differences and case behavior; retain check records. |  |  |
| Expected Results | Battery supplies the eclipse interval; array supply resumes in sunlight; SOC stays within zero to one. |  |  |
| Acceptance Criteria | All applicable signals meet section 5.1 limits, flags and events match expectations, and the expected results in this form hold. |  |  |
| Case Designer |  | Executor / Date | Automated test 2026-10-07 |
| Actual Results | Peak SOC is 100.6153%, above the configured 100% point. Both implementations exhibit this behavior, so overall acceptance fails. 87 checks recorded; evidence: results/DY-002.json. |  |  |
| Recorded By |  | Test Conclusion | [ ] Pass [X] Fail [ ] Not Executed |
| Anomalies | Peak SOC is 100.6153%, above the configured 100% point. Both implementations exhibit this behavior, so overall acceptance fails. |  |  |

DY-002 Scenario Inputs and Initial Conditions

Table 45. DY-002 Scenario Inputs

| Time s | G W/m² | Demand W | Start command |
| --- | --- | --- | --- |
| 0 to 1800 | 1361 | 200 | none |
| 1800 to 3800 | 0 | 200 | none |
| 3800 to 5400 | 1361 | 200 | none |

Initial xn = 0.60, xp = 0.458686001; initial temperature 293.15 K; incidence cosine 1; output interval 20 s.

Parameters not overridden here use sections 5.2 and 6.1.

DY-002 Comparison Results

Figure 14  DY-002: State of charge fraction and Actual solar power W. Top panels show both outputs at identical samples; lower panels show project model minus Simulink in the same units.

The horizontal axis is minutes. Vertical changes retain both sides of a discontinuity at the same time; no interpolation spans that discontinuity.

Table 46. DY-002 Numerical Errors and Limits

| Signal | Max absolute error | RMSE | Limit |
| --- | --- | --- | --- |
| State of charge fraction | 2.84e−07 | 7.69e−08 | 1.00e−06 |
| Actual solar power W | 7.49e−04 | 1.98e−04 | 0.001 |
| Delivered load power W | 1.89e−10 | 2.35e−11 | 0.001 |
| Pack voltage V | 7.15e−08 | 4.38e−08 | 1.00e−04 |
| Pack current A | 2.23e−05 | 5.90e−06 | 1.00e−04 |
| Pack heat W | 4.04e−05 | 8.05e−06 | 0.001 |
| Battery temperature K | 0 | 0 | 0.001 |

Numerical comparison passes; overall acceptance: Fail. Recorded 87 checks.

Peak SOC is 100.6153%, above the configured 100% point. Both implementations exhibit this behavior, so overall acceptance fails.

3.3.3 Test Project 15 Compute load steps

Table 47. DY-003 Test Case

| Case ID | DY-003 | Case Name | Compute load steps |
| --- | --- | --- | --- |
| Test Objective | Verify battery compensation and charge or discharge transitions when compute demand changes. A step is a sudden change of requested power, not a switching-waveform experiment. |  |  |
| Preconditions | Use the frozen section 5 inputs and environment; execute both implementations independently. Design basis: P1–P11. |  |  |
| Input Data | Hold irradiance at 800 W/m² and request 100, 350, 550 and 100 W in consecutive 200 s intervals. Temperature is fixed. Segment boundaries retain both pre-step and post-step values. Exact values appear in the input table for this case. |  |  |
| Procedure | 1. Load this case and run the project model and Simulink independently. 2. Save outputs and events in input order or at the prescribed times. 3. Check validity, same-sample differences and case behavior; retain check records. |  |  |
| Expected Results | Power and current respond to demand steps while lithium states remain continuous at each event. |  |  |
| Acceptance Criteria | All applicable signals meet section 5.1 limits, flags and events match expectations, and the expected results in this form hold. |  |  |
| Case Designer |  | Executor / Date | Automated test 2026-10-07 |
| Actual Results | SOC changes from 65.517% to 71.390%; battery temperature changes from 293.150 K to 293.150 K. 87 checks recorded; evidence: results/DY-003.json. |  |  |
| Recorded By |  | Test Conclusion | [X] Pass [ ] Fail [ ] Not Executed |
| Anomalies | No anomaly against this case criteria. |  |  |

DY-003 Scenario Inputs and Initial Conditions

Table 48. DY-003 Scenario Inputs

| Time s | G W/m² | Demand W | Start command |
| --- | --- | --- | --- |
| 0 to 200 | 800 | 100 | none |
| 200 to 400 | 800 | 350 | none |
| 400 to 600 | 800 | 550 | none |
| 600 to 800 | 800 | 100 | none |

Initial xn = 0.60, xp = 0.458686001; initial temperature 293.15 K; incidence cosine 1; output interval 5 s.

Parameters not overridden here use sections 5.2 and 6.1.

DY-003 Comparison Results

Figure 15  DY-003: Delivered load power W and Pack current A. Top panels show both outputs at identical samples; lower panels show project model minus Simulink in the same units.

The horizontal axis is minutes. Vertical changes retain both sides of a discontinuity at the same time; no interpolation spans that discontinuity.

Table 49. DY-003 Numerical Errors and Limits

| Signal | Max absolute error | RMSE | Limit |
| --- | --- | --- | --- |
| Delivered load power W | 0 | 0 | 0.001 |
| Pack current A | 1.18e−11 | 4.50e−12 | 1.00e−04 |
| Actual solar power W | 3.88e−10 | 1.47e−10 | 0.001 |
| Pack voltage V | 1.13e−12 | 5.61e−13 | 1.00e−04 |
| Pack heat W | 1.40e−11 | 4.34e−12 | 0.001 |
| State of charge fraction | 6.98e−14 | 5.17e−14 | 1.00e−06 |
| Battery temperature K | 0 | 0 | 0.001 |

Numerical comparison passes; overall acceptance: Pass. Recorded 87 checks.

SOC changes from 65.517% to 71.390%; battery temperature changes from 293.150 K to 293.150 K.

3.3.4 Test Project 16 Dynamic charge curtailment

Table 50. DY-004 Test Case

| Case ID | DY-004 | Case Name | Dynamic charge curtailment |
| --- | --- | --- | --- |
| Test Objective | Verify actual solar output and battery heat as the battery state evolves under a charge current limit. |  |  |
| Preconditions | Use the frozen section 5 inputs and environment; execute both implementations independently. Design basis: P1–P11. |  |  |
| Input Data | Run for 900 s at 1800 W/m² and 25 W demand, with cell current bounded below by minus 0.2 A. Other parameters are unchanged; the limit applies to a cell, not the pack current. Exact values appear in the input table for this case. |  |  |
| Procedure | 1. Load this case and run the project model and Simulink independently. 2. Save outputs and events in input order or at the prescribed times. 3. Check validity, same-sample differences and case behavior; retain check records. |  |  |
| Expected Results | Charging respects limits, curtailment follows charge capability, and both trajectories agree. |  |  |
| Acceptance Criteria | All applicable signals meet section 5.1 limits, flags and events match expectations, and the expected results in this form hold. |  |  |
| Case Designer |  | Executor / Date | Automated test 2026-10-07 |
| Actual Results | SOC changes from 65.517% to 67.326%; battery temperature changes from 293.150 K to 293.150 K. 87 checks recorded; evidence: results/DY-004.json. |  |  |
| Recorded By |  | Test Conclusion | [X] Pass [ ] Fail [ ] Not Executed |
| Anomalies | No anomaly against this case criteria. |  |  |

DY-004 Scenario Inputs and Initial Conditions

Table 51. DY-004 Scenario Inputs

| Time s | G W/m² | Demand W | Start command |
| --- | --- | --- | --- |
| 0 to 900 | 1800 | 25 | none |

Initial xn = 0.60, xp = 0.458686001; initial temperature 293.15 K; incidence cosine 1; output interval 10 s.

Overrides imin = −0.2

Parameters not overridden here use sections 5.2 and 6.1.

DY-004 Comparison Results

Figure 16  DY-004: Cell current A and Actual solar power W. Top panels show both outputs at identical samples; lower panels show project model minus Simulink in the same units.

The horizontal axis is minutes. Vertical changes retain both sides of a discontinuity at the same time; no interpolation spans that discontinuity.

Table 52. DY-004 Numerical Errors and Limits

| Signal | Max absolute error | RMSE | Limit |
| --- | --- | --- | --- |
| Cell current A | 0 | 0 | 1.00e−04 |
| Actual solar power W | 4.97e−14 | 2.64e−14 | 0.001 |
| Delivered load power W | 0 | 0 | 0.001 |
| Pack voltage V | 4.97e−14 | 2.77e−14 | 1.00e−04 |
| Pack current A | 0 | 0 | 1.00e−04 |
| Pack heat W | 7.89e−17 | 1.52e−17 | 0.001 |
| State of charge fraction | 4.44e−16 | 2.88e−16 | 1.00e−06 |
| Battery temperature K | 0 | 0 | 0.001 |

Numerical comparison passes; overall acceptance: Pass. Recorded 87 checks.

SOC changes from 65.517% to 67.326%; battery temperature changes from 293.150 K to 293.150 K.

3.3.5 Test Project 17 Supply loss latch and explicit restart

Table 53. DY-005 Test Case

| Case ID | DY-005 | Case Name | Supply loss latch and explicit restart |
| --- | --- | --- | --- |
| Test Objective | Verify supply loss, latching, sunlight recovery, explicit restart and a subsequent stop. Protection must change load connectivity while allowing charging with the load disconnected. |  |  |
| Preconditions | Use the frozen section 5 inputs and environment; execute both implementations independently. Design basis: P1–P11. |  |  |
| Input Data | At 100 s remove sunlight and request 2500 W. Restore normal sunlight at 200 s without a start command; start at 300 s, stop at 400 s and start again at 500 s. End at 600 s. Exact values appear in the input table for this case. |  |  |
| Procedure | 1. Load this case and run the project model and Simulink independently. 2. Save outputs and events in input order or at the prescribed times. 3. Check validity, same-sample differences and case behavior; retain check records. |  |  |
| Expected Results | Trip at 100 s; sunlight at 200 s causes no restart; start at 300 s, stop at 400 s, and restart at 500 s. |  |  |
| Acceptance Criteria | All applicable signals meet section 5.1 limits, flags and events match expectations, and the expected results in this form hold. |  |  |
| Case Designer |  | Executor / Date | Automated test 2026-10-07 |
| Actual Results | Supply trips at 100 s; the load remains disconnected after sunlight returns at 200 s. Explicit start at 300 s, stop at 400 s and restart at 500 s agree with expectations. 88 checks recorded; evidence: results/DY-005.json. |  |  |
| Recorded By |  | Test Conclusion | [X] Pass [ ] Fail [ ] Not Executed |
| Anomalies | No anomaly against this case criteria. |  |  |

DY-005 Scenario Inputs and Initial Conditions

Table 54. DY-005 Scenario Inputs

| Time s | G W/m² | Demand W | Start command |
| --- | --- | --- | --- |
| 0 to 100 | 1361 | 200 | none |
| 100 to 200 | 0 | 2500 | none |
| 200 to 300 | 1361 | 200 | none |
| 300 to 400 | 1361 | 200 | start |
| 400 to 500 | 1361 | 200 | stop |
| 500 to 600 | 1361 | 200 | start |

Initial xn = 0.60, xp = 0.458686001; initial temperature 293.15 K; incidence cosine 1; output interval 5 s.

Parameters not overridden here use sections 5.2 and 6.1.

DY-005 Comparison Results

Figure 17  DY-005: Load connected flag and Delivered load power W. Top panels show both outputs at identical samples; lower panels show project model minus Simulink in the same units.

The horizontal axis is minutes. Vertical changes retain both sides of a discontinuity at the same time; no interpolation spans that discontinuity.

Table 55. DY-005 Numerical Errors and Limits

| Signal | Max absolute error | RMSE | Limit |
| --- | --- | --- | --- |
| Load connected flag | 0 | 0 | 0 |
| Delivered load power W | 0 | 0 | 0.001 |
| Actual solar power W | 6.55e−10 | 1.57e−10 | 0.001 |
| Pack voltage V | 1.44e−12 | 3.47e−13 | 1.00e−04 |
| Pack current A | 1.92e−11 | 4.61e−12 | 1.00e−04 |
| Pack heat W | 3.63e−11 | 8.72e−12 | 0.001 |
| State of charge fraction | 1.93e−14 | 6.18e−15 | 1.00e−06 |
| Battery temperature K | 0 | 0 | 0.001 |

Numerical comparison passes; overall acceptance: Pass. Recorded 88 checks.

Supply trips at 100 s; the load remains disconnected after sunlight returns at 200 s. Explicit start at 300 s, stop at 400 s and restart at 500 s agree with expectations.

3.3.6 Test Project 18 Battery electrothermal feedback

Table 56. DY-006 Test Case

| Case ID | DY-006 | Case Name | Battery electrothermal feedback |
| --- | --- | --- | --- |
| Test Objective | Verify the loop in which battery heat changes temperature, which in turn changes voltage and current. The thermal boundary is a prescribed heat-sink temperature, not ambient-air convection. |  |  |
| Preconditions | Use the frozen section 5 inputs and environment; execute both implementations independently. Design basis: P1–P11. |  |  |
| Input Data | Use no solar power, a 200 W load, initial battery temperature 283.15 K, heat capacity 5000 J/K, thermal resistance 0.8 K/W and a 273.15 K sink for 1800 s. This is a one-node battery thermal test, not full six-node Thermal integration. Exact values appear in the input table for this case. |  |  |
| Procedure | 1. Load this case and run the project model and Simulink independently. 2. Save outputs and events in input order or at the prescribed times. 3. Check validity, same-sample differences and case behavior; retain check records. |  |  |
| Expected Results | Temperature is integrated once; heat generation and rejection determine temperature and feed back into voltage and current. |  |  |
| Acceptance Criteria | All applicable signals meet section 5.1 limits, flags and events match expectations, and the expected results in this form hold. |  |  |
| Case Designer |  | Executor / Date | Automated test 2026-10-07 |
| Actual Results | SOC changes from 65.517% to 44.282%; battery temperature changes from 283.150 K to 280.874 K. 85 checks recorded; evidence: results/DY-006.json. |  |  |
| Recorded By |  | Test Conclusion | [X] Pass [ ] Fail [ ] Not Executed |
| Anomalies | No anomaly against this case criteria. |  |  |

DY-006 Scenario Inputs and Initial Conditions

Table 57. DY-006 Scenario Inputs

| Time s | G W/m² | Demand W | Start command |
| --- | --- | --- | --- |
| 0 to 1800 | 0 | 200 | none |

Initial xn = 0.60, xp = 0.458686001; initial temperature 283.15 K; incidence cosine 1; output interval 10 s.

CB = 5000 J/K; R = 0.8 K/W; Tsink = 273.15 K.

Parameters not overridden here use sections 5.2 and 6.1.

DY-006 Comparison Results

Figure 18  DY-006: Battery temperature K and Pack heat W. Top panels show both outputs at identical samples; lower panels show project model minus Simulink in the same units.

The horizontal axis is minutes. Vertical changes retain both sides of a discontinuity at the same time; no interpolation spans that discontinuity.

Table 58. DY-006 Numerical Errors and Limits

| Signal | Max absolute error | RMSE | Limit |
| --- | --- | --- | --- |
| Battery temperature K | 8.53e−13 | 3.79e−13 | 0.001 |
| Pack heat W | 1.44e−12 | 1.62e−13 | 0.001 |
| Actual solar power W | 0 | 0 | 0.001 |
| Delivered load power W | 3.48e−11 | 3.90e−12 | 0.001 |
| Pack voltage V | 8.53e−14 | 3.20e−14 | 1.00e−04 |
| Pack current A | 1.24e−12 | 1.39e−13 | 1.00e−04 |
| State of charge fraction | 9.99e−16 | 4.34e−16 | 1.00e−06 |

Numerical comparison passes; overall acceptance: Pass. Recorded 85 checks.

SOC changes from 65.517% to 44.282%; battery temperature changes from 283.150 K to 280.874 K.

3.3.7 Test Project 19 Energy balance over three orbit cycles

Table 59. DY-007 Test Case

| Case ID | DY-007 | Case Name | Energy balance over three orbit cycles |
| --- | --- | --- | --- |
| Test Objective | Verify cumulative energy and state drift over repeated sunlight and eclipse cycles. Long trajectories can expose missing charge boundaries despite correct instantaneous power balance. |  |  |
| Preconditions | Use the frozen section 5 inputs and environment; execute both implementations independently. Design basis: P1–P11. |  |  |
| Input Data | Repeat the controlled DY-002 cycle three times for 16200 s. Save every 30 s and retain both sides of all eclipse entry and exit boundaries. Exact values appear in the input table for this case. |  |  |
| Procedure | 1. Load this case and run the project model and Simulink independently. 2. Save outputs and events in input order or at the prescribed times. 3. Check validity, same-sample differences and case behavior; retain check records. |  |  |
| Expected Results | Conservation holds over three cycles, integrated energies agree, and SOC stays within zero to one. |  |  |
| Acceptance Criteria | All applicable signals meet section 5.1 limits, flags and events match expectations, and the expected results in this form hold. |  |  |
| Case Designer |  | Executor / Date | Automated test 2026-10-07 |
| Actual Results | Peak SOC is 104.2070%, above the configured 100% point. Both implementations exhibit this behavior, so overall acceptance fails. 87 checks recorded; evidence: results/DY-007.json. |  |  |
| Recorded By |  | Test Conclusion | [ ] Pass [X] Fail [ ] Not Executed |
| Anomalies | Peak SOC is 104.2070%, above the configured 100% point. Both implementations exhibit this behavior, so overall acceptance fails. |  |  |

DY-007 Scenario Inputs and Initial Conditions

Table 60. DY-007 Scenario Inputs

| Time s | G W/m² | Demand W | Start command |
| --- | --- | --- | --- |
| 0 to 1800 | 1361 | 200 | none |
| 1800 to 3800 | 0 | 200 | none |
| 3800 to 5400 | 1361 | 200 | none |
| 5400 to 7200 | 1361 | 200 | none |
| 7200 to 9200 | 0 | 200 | none |
| 9200 to 10800 | 1361 | 200 | none |
| 10800 to 12600 | 1361 | 200 | none |
| 12600 to 14600 | 0 | 200 | none |
| 14600 to 16200 | 1361 | 200 | none |

Initial xn = 0.60, xp = 0.458686001; initial temperature 293.15 K; incidence cosine 1; output interval 30 s.

Parameters not overridden here use sections 5.2 and 6.1.

DY-007 Comparison Results

Figure 19  DY-007: State of charge fraction and Actual solar power W. Top panels show both outputs at identical samples; lower panels show project model minus Simulink in the same units.

The horizontal axis is minutes. Vertical changes retain both sides of a discontinuity at the same time; no interpolation spans that discontinuity.

Table 61. DY-007 Numerical Errors and Limits

| Signal | Max absolute error | RMSE | Limit |
| --- | --- | --- | --- |
| State of charge fraction | 2.81e−07 | 5.56e−08 | 1.00e−06 |
| Actual solar power W | 7.39e−04 | 1.43e−04 | 0.001 |
| Delivered load power W | 1.80e−10 | 2.08e−11 | 0.001 |
| Pack voltage V | 7.15e−08 | 2.95e−08 | 1.00e−04 |
| Pack current A | 2.20e−05 | 4.26e−06 | 1.00e−04 |
| Pack heat W | 3.94e−05 | 5.66e−06 | 0.001 |
| Battery temperature K | 0 | 0 | 0.001 |

Numerical comparison passes; overall acceptance: Fail. Recorded 87 checks.

Peak SOC is 104.2070%, above the configured 100% point. Both implementations exhibit this behavior, so overall acceptance fails.

3.4 Numerical Accuracy Review

3.4.1 Test Project 20 Solver convergence and accuracy review

Table 62. NU-001 Test Case

| Case ID | NU-001 | Case Name | Solver convergence and accuracy review |
| --- | --- | --- | --- |
| Test Objective | Check whether numerical precision explains the observed difference. Independently tighten both solvers and reduce the maximum step, requiring changes below one tenth of the original acceptance limit. |  |  |
| Preconditions | Use the frozen section 5 inputs and environment; execute both implementations independently. Design basis: P1–P11. |  |  |
| Input Data | Run 1200 s with no solar input, a 200 W load, initial battery temperature 293.15 K and a 283.15 K sink. Tighten relative tolerance from 10 to the power minus 8 to 10 to the power minus 10 and reduce maximum step from 10 s to 2 s. Exact values appear in the input table for this case. |  |  |
| Procedure | 1. Load this case and run the project model and Simulink independently. 2. Save outputs and events in input order or at the prescribed times. 3. Check validity, same-sample differences and case behavior; retain check records. |  |  |
| Expected Results | Each solver changes by less than one tenth of the corresponding comparison limit under independent refinement. |  |  |
| Acceptance Criteria | All applicable signals meet section 5.1 limits, flags and events match expectations, and the expected results in this form hold. |  |  |
| Case Designer |  | Executor / Date | Automated test 2026-10-07 |
| Actual Results | SOC changes from 65.517% to 51.553%; battery temperature changes from 293.150 K to 291.345 K. 95 checks recorded; evidence: results/NU-001.json. |  |  |
| Recorded By |  | Test Conclusion | [X] Pass [ ] Fail [ ] Not Executed |
| Anomalies | No anomaly against this case criteria. |  |  |

NU-001 Scenario Inputs and Initial Conditions

Table 63. NU-001 Scenario Inputs

| Time s | G W/m² | Demand W | Start command |
| --- | --- | --- | --- |
| 0 to 1200 | 0 | 200 | none |

Initial xn = 0.60, xp = 0.458686001; initial temperature 293.15 K; incidence cosine 1; output interval 10 s.

CB = 5000 J/K; R = 0.8 K/W; Tsink = 283.15 K.

Parameters not overridden here use sections 5.2 and 6.1.

NU-001 Comparison Results

Figure 20  NU-001: Battery temperature K and Pack voltage V. Top panels show both outputs at identical samples; lower panels show project model minus Simulink in the same units.

The horizontal axis is minutes. Vertical changes retain both sides of a discontinuity at the same time; no interpolation spans that discontinuity.

Table 64. NU-001 Numerical Errors and Limits

| Signal | Max absolute error | RMSE | Limit |
| --- | --- | --- | --- |
| Battery temperature K | 9.66e−13 | 4.79e−13 | 0.001 |
| Pack voltage V | 1.17e−13 | 3.25e−14 | 1.00e−04 |
| Actual solar power W | 0 | 0 | 0.001 |
| Delivered load power W | 3.43e−11 | 4.32e−12 | 0.001 |
| Pack current A | 1.22e−12 | 1.53e−13 | 1.00e−04 |
| Pack heat W | 1.18e−12 | 1.51e−13 | 0.001 |
| State of charge fraction | 1.11e−15 | 4.88e−16 | 1.00e−06 |

Numerical comparison passes; overall acceptance: Pass. Recorded 95 checks.

SOC changes from 65.517% to 51.553%; battery temperature changes from 293.150 K to 291.345 K.

4 Test Content Sufficiency Analysis

Table 65. Test Coverage

| Capability | Cases | Verified Focus |
| --- | --- | --- |
| Solar Array and Battery Components | PV-001, BT-001, BT-002, BT-003, BT-004 | Component response, boundary inputs and independent comparison |
| Power Allocation and Protection Interfaces | PD-001, PD-002, CT-001, CT-002, CT-003, PR-001, IV-001 | Component response, boundary inputs and independent comparison |
| Dynamic Supply and Electrothermal Processes | DY-001, DY-002, DY-003, DY-004, DY-005, DY-006, DY-007 | Dynamic states, events, energy or convergence checks |
| Numerical Accuracy Review | NU-001 | Dynamic states, events, energy or convergence checks |

This report verifies implementations of the same equations and the listed design behaviors. It does not cover measured-cell accuracy, rapid diffusion relaxation, high-rate electrolyte effects, switching ripple, MPPT tracking transients, autonomous event localization during continuous depletion, full six-node Thermal integration, or every SimReady asset error. Scheduled-boundary protection is covered; this is not evidence of all continuous-boundary localization behavior.

All 20 cases executed, but coverage does not mean all acceptance criteria passed. CT-003, DY-002 and DY-007 require correction of full-charge constraints and retesting. Physical accuracy and broader system integration need additional tests.

5 Test Conditions and Requirements

5.1 Execution Environment and Acceptance Criteria

Table 66. Numerical and Behavioral Acceptance Criteria

| Quantity | Maximum absolute difference |
| --- | --- |
| Static power and heat | 0.000001 W |
| Dynamic power and heat | 0.001 W |
| Voltage | 0.0001 V |
| Current | 0.0001 A |
| SOC and lithium fractions | 0.000001 |
| Battery temperature | 0.001 K |
| Lithium fraction derivative | 0.00000001 s⁻¹ |
| Discrete flags and reason codes | Exact agreement |
| Scheduled event time | 0.001 s |
| Relative integrated energy difference | 0.00001 |
| Power conservation residual | 0.000002 W |
| Relative lithium inventory drift | 0.0000000001 |
| Usable SOC range | 0 to 1, with a 0.000001 rounding allowance |
| Full-charge boundary | At SOC 1, cell current must be at least minus 0.00000001 A |

Numerical thresholds assess software consistency, not measured cell accuracy. RMSE is reported alongside maximum error; every applicable signal must meet its maximum-error limit. Refinement changes must be below one tenth of the corresponding limit.

Input version 1.0 was frozen before initial execution. Coverage review added CT-003 and SOC behavior criteria in version 1.1 after identifying missing full-charge coverage. Numerical thresholds remain unchanged; prior inputs and criteria are retained in results/history.

MATLAB R2026b 26.2.0.3386108; Simulink 26.2; Windows; Python Thermal/.venv; SciPy DOP853.

Baseline integration uses relative tolerance 10⁻⁸, absolute tolerance 10⁻¹⁰ and maximum step 10 s. Refinement uses 10⁻¹⁰, 10⁻¹² and 2 s.

5.2 Baseline Scenario and Input Requirements

Table 67. Baseline Parameters and Physical Meaning

| Input | Value | Meaning |
| --- | --- | --- |
| A | 1.8 m² | Active solar cell area |
| ηpv | 0.30 | Fixed maximum-power-point efficiency |
| G | 1361 W/m² | Nominal illumination; zero denotes eclipse. Eclipse is already included and is not multiplied twice. |
| cos θ | 1 | Normal incidence; zero is edge-on and negative is rear-face illumination. |
| Ns × Np | 8 × 6 | Eight series cells per string and six parallel strings, totaling 48 identical cells. |
| ηD | 0.95 | Efficiency of distribution and its load-side harness |
| RΩ | 0.025 Ω | Cell ohmic resistance |
| TB | 293.15 K / 20 ℃ | Initial or prescribed battery temperature, not space ambient air. |
| xn / xp | 0.600000 / 0.458686001 | Mean electrode lithium fractions, dimensionless |
| SOC | 65.517241% | Usable state of charge derived from negative fraction |
| xn,0 / xn,100 / xp,100 | 0.03 / 0.90 / 0.27 | Empty and full-charge endpoints from the same parameter set |
| Cell current range | −3 to 6 A | Negative for charging, positive for discharge |
| Cell voltage range | 3.0 to 4.2 V | Cell terminal voltage constraint |
| Material ranges | xn: 0.01 to 0.95; xp: 0.20 to 0.95 | Constraints on mean, center and surface fractions; not equivalent to the usable SOC interval 0 to 1. |

Unless explicitly overridden, cases use this table and the material parameters in section 6.1. Illumination and idealized cycles are controlled inputs, not actual ISS conditions. Low and high temperature refer to specified battery temperatures.

In input tables, imin and imax are cell charge and discharge current bounds in A; vmin and vmax are cell voltage limits in V; eta is distribution efficiency. Logical flags use 1 for true and 0 for false. Exact inputs are retained in suite.json; displayed table values may be rounded.

6 Test Data

6.1 Battery Material Parameters

Table 68. Battery Material Parameters

| Parameter | Negative electrode | Positive electrode |
| --- | --- | --- |
| Particle radius m | 6.00e−06 | 5.00e−06 |
| Active material volume fraction | 0.75 | 0.665 |
| Effective electrode area m² | 0.06 | 0.06 |
| Electrode thickness m | 8.50e−05 | 7.50e−05 |
| Maximum lithium concentration mol/m³ | 31000 | 63000 |
| Reference diffusion coefficient m²/s | 3.30e−14 | 1.00e−14 |
| Reference exchange current A | 2.5 | 3 |
| Diffusion activation energy J/mol | 30300 | 25000 |
| Reaction activation energy J/mol | 35000 | 17500 |
| Equilibrium potential polynomial coefficients V | 0.65, −1.6, 2, −0.95 | 4.6, −1.3, 0.9, −0.8 |
| Temperature polynomial coefficients V/K | 1.20e−04, −3.00e−04, 1.50e−04, 0 | −6.00e−05, 4.00e−05, 0, 0 |

Polynomial coefficients run from constant term to highest power, with reference temperature 298.15 K. Electrode charge is Qk = F εk Ael Lk ck,max, the charge for a fraction change from 0 to 1 rather than a directly specified rated Ah capacity. These are existing illustrative test values, not a selected or calibrated cell.

Sources and constraints

Power/SDTwin_Power_Design_Report_CN.docx; Power/SDTwin_Power_Design_Report_EN.docx; Thermal/sdtwin_sim/power_stand_in.py, example_power_records.

The material temperature range is 253.15 to 333.15 K. Cell ohmic loss is included in battery heat; distribution efficiency covers the PDU-to-Compute harness to avoid duplicate loss accounting.

6.2 Data Inventory and Reproduction

Use C:/Workspace/SpaceDC as the working directory. Run the following sequence to regenerate fixtures, independent results, verdicts and reports.

Thermal/.venv/Scripts/python.exe Power/verification/prepare.py

Thermal/.venv/Scripts/python.exe Power/verification/run_python.py

matlab -batch "addpath('Power/verification/matlab'); run_suite"

Thermal/.venv/Scripts/python.exe Power/verification/compare.py

python Power/verification/build_report.py

Use a document runtime with python-docx and matplotlib for the last command. Replace matlab with the full local R2026b executable path when needed.

Table 69. Data Inventory and Reproduction

| File | Content |
| --- | --- |
| results/suite.json | Complete parameters, cases and criteria |
| matlab/sdtwin_power_reference.slx | Executed Simulink model |
| matlab/power_reference.m | Independent reference equations |
| results/<ID>_python.csv / <ID>_simulink.csv | Raw results from both implementations |
| results/<ID>_difference.csv | Direct differences at shared samples |
| results/<ID>.json / summary.json | All checks, errors and verdicts |
| results/<ID>_*_events.json | Actual event times and connectivity |
| results/NU-001_*_fine.csv | Independent refinement runs |
| results/history | Original inputs and criteria before coverage expansion |

Input SHA256: f2d46a239842d0bba55d537efc8a793bb2c4df4644c4ca461afc9058a2400757

The implementation uses MathWorks Level 2 MATLAB S-function interfaces. The Simulink engine manages continuous states through Derivatives and InitializeConditions callbacks.

https://www.mathworks.com/help/simulink/sfg/writing-level-2-matlab-s-functions.html

6.3 Integrated Energy Comparison Data

Integrate each output series with the trapezoidal rule. Left and right event values have identical time, so their interval contributes zero energy. This compares energy at the common output cadence, not additional measured energy.

DY-002

Table 70. Integrated Energy Comparison Data

| Energy source | Project J | Simulink J | Relative difference |
| --- | --- | --- | --- |
| Battery terminal power | −718286 | −718286 | 7.62e−07 |
| Delivered load power | 1.08e+06 | 1.08e+06 | 1.36e−14 |
| Actual solar power | 1.85513e+06 | 1.85513e+06 | 2.95e−07 |
| Pack heat | 31993.8 | 31993.8 | 5.84e−07 |
| Distribution loss | 56842.1 | 56842.1 | 1.40e−14 |

DY-007

Table 71. Integrated Energy Comparison Data

| Energy source | Project J | Simulink J | Relative difference |
| --- | --- | --- | --- |
| Battery terminal power | −768115 | −768114 | 1.23e−06 |
| Delivered load power | 3.24e+06 | 3.24e+06 | 1.03e−14 |
| Actual solar power | 4.17864e+06 | 4.17864e+06 | 2.25e−07 |
| Pack heat | 58964.7 | 58964.7 | 4.62e−07 |
| Distribution loss | 170526 | 170526 | 1.08e−14 |

Battery terminal energy is signed: positive for net discharge and negative for net charge. Battery heat and distribution loss are integrated separately; internal heat is not added to terminal-power balance. Passing energy comparison does not change the failed SOC acceptance of these cases.

6.4 Numerical Convergence Data

NU-001 refines Python and Simulink separately. Each entry is the maximum absolute difference between baseline and refined runs of the same solver, not the difference between the two programs.

Table 72. Numerical Convergence Data

| Solver | Quantity | Maximum change | Allowed change |
| --- | --- | --- | --- |
| python | State of charge fraction | 1.55e−15 | 1.00e−07 |
| python | Pack voltage V | 1.78e−14 | 1.00e−05 |
| python | Pack current A | 4.44e−15 | 1.00e−05 |
| python | Pack heat W | 2.89e−14 | 1.00e−04 |
| python | Battery temperature K | 5.68e−13 | 1.00e−04 |
| simulink | State of charge fraction | 9.99e−16 | 1.00e−07 |
| simulink | Pack voltage V | 1.03e−13 | 1.00e−05 |
| simulink | Pack current A | 1.07e−14 | 1.00e−05 |
| simulink | Pack heat W | 3.02e−14 | 1.00e−04 |
| simulink | Battery temperature K | 1.02e−12 | 1.00e−04 |

Both solvers meet the refinement criterion of one tenth of the acceptance threshold. This check covers this smooth electrothermal scenario, not all stiff regimes or autonomous protection-event localization accuracy.

7 Test Summary

This report records the framework, inputs, criteria and individual comparisons of the Power model with independent Simulink simulation. All 20 numerical comparisons pass; 17 cases pass design acceptance and 3 fail due to the full-charge constraint.

Table 73. Power Module Test Summary

| No. | Case ID | Function | Verification Focus | Status | Result / Evidence |
| --- | --- | --- | --- | --- | --- |
| 1 | PV-001 | solar_power | Solar irradiance and panel attitude | Pass | Completed 21 input combinations. Output availability, discrete status and applicable numerical difference checks pass. results/PV-001.json |
| 2 | BT-001 | battery_response | Open circuit voltage and initial charge | Pass | Completed 9 input combinations. Output availability, discrete status and applicable numerical difference checks pass. results/BT-001.json |
| 3 | BT-002 | battery_response | Charge and discharge voltage versus temperature | Pass | Completed 18 input combinations. Output availability, discrete status and applicable numerical difference checks pass. results/BT-002.json |
| 4 | BT-003 | battery_response | Battery heat and reversible heat sign | Pass | Pack heat ranges from −0.0320434 to 3.23576 W; negative heat is retained. results/BT-003.json |
| 5 | BT-004 | battery_response | Cell to series and parallel pack scaling | Pass | Completed 5 input combinations. Output availability, discrete status and applicable numerical difference checks pass. results/BT-004.json |
| 6 | PD-001 | solve_power_allocation | Solar and battery power allocation | Pass | Completed 24 input combinations. Output availability, discrete status and applicable numerical difference checks pass. results/PD-001.json |
| 7 | PD-002 | solve_power_allocation | Distribution efficiency and loss | Pass | Completed 9 input combinations. Output availability, discrete status and applicable numerical difference checks pass. results/PD-002.json |
| 8 | CT-001 | solve_power_allocation | Charge limits and solar curtailment | Pass | Completed 6 input combinations. Output availability, discrete status and applicable numerical difference checks pass. results/CT-001.json |
| 9 | CT-002 | solve_power_allocation | Discharge capability and supply shortfall | Pass | Completed 12 input combinations. Output availability, discrete status and applicable numerical difference checks pass. results/CT-002.json |
| 10 | CT-003 | solve_power_allocation | Charging boundary at full state of charge | Fail | All three full-charge samples continue charging, with minimum cell current −0.544984 A. Numerical agreement passes, but the full-charge requirement fails. results/CT-003.json |
| 11 | PR-001 | apply_power_event | Protection commands and latched states | Pass | Completed 8 input combinations. Output availability, discrete status and applicable numerical difference checks pass. results/PR-001.json |
| 12 | IV-001 | PowerInputs / PowerState | Invalid inputs and state boundaries | Pass | Completed 6 input combinations. Output availability, discrete status and applicable numerical difference checks pass. results/IV-001.json |
| 13 | DY-001 | solve_power_allocation / state integration | Charging under continuous sunlight | Pass | SOC changes from 65.517% to 88.654%; battery temperature changes from 293.150 K to 293.150 K. results/DY-001.json |
| 14 | DY-002 | solve_power_allocation / state integration | Eclipse entry and exit | Fail | Peak SOC is 100.6153%, above the configured 100% point. Both implementations exhibit this behavior, so overall acceptance fails. results/DY-002.json |
| 15 | DY-003 | solve_power_allocation / state integration | Compute load steps | Pass | SOC changes from 65.517% to 71.390%; battery temperature changes from 293.150 K to 293.150 K. results/DY-003.json |
| 16 | DY-004 | solve_power_allocation / state integration | Dynamic charge curtailment | Pass | SOC changes from 65.517% to 67.326%; battery temperature changes from 293.150 K to 293.150 K. results/DY-004.json |
| 17 | DY-005 | solve_power_allocation / state integration | Supply loss latch and explicit restart | Pass | Supply trips at 100 s; the load remains disconnected after sunlight returns at 200 s. Explicit start at 300 s, stop at 400 s and restart at 500 s agree with expectations. results/DY-005.json |
| 18 | DY-006 | solve_power_allocation / state integration | Battery electrothermal feedback | Pass | SOC changes from 65.517% to 44.282%; battery temperature changes from 283.150 K to 280.874 K. results/DY-006.json |
| 19 | DY-007 | solve_power_allocation / state integration | Energy balance over three orbit cycles | Fail | Peak SOC is 104.2070%, above the configured 100% point. Both implementations exhibit this behavior, so overall acceptance fails. results/DY-007.json |
| 20 | NU-001 | DOP853 / ode45 | Solver convergence and accuracy review | Pass | SOC changes from 65.517% to 51.553%; battery temperature changes from 293.150 K to 291.345 K. results/NU-001.json |

7.1 Anomalies and Conclusion

All 20 projects completed. Numerical agreement passes in 20 cases; design acceptance passes in 17 and fails in 3. The three failures expose the same omitted full-charge constraint in static and dynamic conditions.

Table 74. Anomalies and Verdicts

| Case | Project result | Reason |
| --- | --- | --- |
| CT-003 | Charging at about minus 0.545 A per cell at SOC 1 | No stop at the configured full-charge endpoint |
| DY-002 | Peak SOC 100.6153% | Full charge exceeded in one cycle |
| DY-007 | Peak SOC 104.2070% | Repeated cycles further expose the overcharge state |

Code evidence: _linear_limit checks current and particle surface or center fractions, and _search additionally checks terminal voltage. The xn,100 endpoint used to compute SOC is absent from charging limits. The independently implemented Simulink equations reproduce this behavior. Evidence supports a mismatch between the constraint set and the full-charge requirement, rather than an integration error.

Recommended correction: explicitly decide that usable SOC endpoints are charge and discharge constraints, reallocate at accepted boundary events, and curtail surplus solar at full charge. Rerun CT-003, DY-002, DY-007 and the regression suite after correction. Clipping displayed SOC to 1 is insufficient.

Overall Conclusion: [ ] Pass   [X] Fail   [ ] Not Executed. All 20 numerical comparisons pass; three design-behavior cases fail acceptance.

On-site Test Expert Signature: ________________________    Date: ________________